ITEM MO-120  AIRPORT PRECISION APPROACH PATH INDICATOR (PAPI) SYSTEM

# DESCRIPTION

120-1.1  This item consists of Precision Approach Path Indicator (PAPI) system furnished and installed in accordance with this specification, the referenced specifications, and the applicable Federal Aviation Administration (FAA) Advisory Circulars. The system shall be installed at the locations and in accordance with the dimensions, design, and details shown in the plans. This item includes the furnishing of all equipment, materials, services, testing, and incidentals necessary to place the systems in operation as completed units to the satisfaction of the Engineer.

Requirements and payments for underground cable from the vault to the power and control unit, and electrical controls and vault work will be measured and paid for separately as specified in Item MO-108 “Underground Power Cable for Airports” and Item MO-109 “Airport Prefabricated Housing and Equipment”.

120-1.2  The Contractor is responsible for using the current versions of the referenced FAA Advisory Circulars, including any changes, in effect at the time of bidding. The advisory circulars may be viewed on the FAA website at the following address:

http://www.faa.gov/arp/150acs.cfm

# EQUIPMENT AND MATERIALS

120-2.1  GENERAL.

a.  Airport lighting equipment and materials covered by Federal Aviation Administration (FAA) specifications shall be approved under the Airport Lighting Equipment Certification Program described in Advisory Circular (AC) 150/5345-53, current version.

b.  All other equipment and materials covered by other referenced specifications shall be subject to acceptance through manufacturer's certification of compliance with the applicable specification, when requested by the Engineer.

c.  Manufacturer's certifications shall not relieve the Contractor of the Contractor’s responsibility to provide materials in accordance with these specifications and acceptable to the Engineer.  Materials supplied and/or installed that do not materially comply with these specifications shall be removed, when directed by the Engineer and replaced with materials, which do comply with these specifications, at the sole cost of the Contractor.

d.  All materials and equipment used to construct this item shall be submitted to the Engineer for approval prior to ordering the equipment.  Submittals consisting of marked catalog sheets or shop drawings shall be provided.  Submittal data shall be presented in a clear, precise and thorough manner.  Original catalog sheets are preferred.  Photocopies are acceptable provided they are as good a quality as the original.  Clearly and boldly mark each copy to identify pertinent products or models applicable to this project.  Indicate all optional equipment and delete non-pertinent data.  Submittals for components of electrical equipment and systems shall identify the equipment for which they apply on each submittal sheet.  Markings shall be boldly and clearly made with arrows or circles (highlighting is not acceptable).  Contractor is solely responsible for delays in project accruing directly or indirectly from late submissions or resubmissions of submittals.

e.  The data submitted shall be sufficient, in the opinion of the Engineer, to determine compliance with the plans and specifications.  The Contractor's submittals (five (5) copies) shall be neatly bound in a properly sized 3-ring binder, tabbed by specification section.  The Engineer reserves the right to reject any and all equipment, materials or procedures, which, in the Engineer’s opinion, does not meet the system design and the standards and codes, specified herein.

f.  All equipment and materials furnished and installed under this section shall be guaranteed against defects in materials and workmanship for a period of at least twelve (12) months from final acceptance by the Owner.  The defective materials and/or equipment shall be repaired or replaced, at the Owner's discretion, with no additional cost to the Owner.  The Contractor shall be responsible to maintain an insulation resistance of 50 megohms minima, (1000V megger) with isolation transformers connected in new circuits and new segments of existing circuits through the end of the contract warranty period.

120-2.2  STEEL CONDUIT.  Rigid galvanized steel conduit and fittings shall be hot dipped galvanized inside and out and conform to the requirements of Underwriters Laboratories Standard 6, 514B, and 1242.

120-2.3  PLASTIC CONDUIT.  Plastic conduit and fittings-shall conform to the requirements of Fed. Spec. W-C-1094, Underwriters Laboratories Standards UL-651 and Article 347 of the current National Electrical Code shall be one of the following, as shown on the plans:

a. Type I–Schedule 40 PVC suitable for underground use either direct-buried or encased in concrete.

b. Type II–Schedule 40 PVC suitable for either above ground or underground use.

The type of adhesive shall be as recommended by the conduit/fitting manufacturer.

120-2.4  CONCRETE.  The concrete for bases, footings, etc. shall be proportioned, placed, and cured in accordance with Item MO-610, “Structural Portland Cement Concrete.”

120-2.5  LIGHT BASES AND TRANSFORMER HOUSINGS.  Light bases and transformer housings shall be Type L-867 conforming to the requirements AC 150/5345-42. The sizes of the units and any accessories shall be as shown on the plans.

120-2.6  CABLE.  Underground cable for use between PAPI light units shall conform to the requirements of MO-108 “Underground Power Cable for Airports. The size and type of the cable shall be as shown on the plans or per the manufacturer’s recommendations.

120-2.7  ISOLATION TRANSFORMERS.  Isolation transformers shall be rated 6.6/6.6 amperes and sized for the light or equipment being served. All isolation transformers shall be Type L-830 conforming to the requirements of AC 150/5345-47.

120-2.8  PAPI SYSTEM.  The PAPI system shall be Type L-880, Style B, Class I, conforming to the requirements of AC 150/5345-28. The system shall consist of the following components:

a.  Four identical PAPI light units.

b.  Aiming and calibration equipment.

120-2.9  EXISTING CIRCUITS.  Whenever the scope of work requires, connection to an existing circuit, the circuit’s insulation resistance shall be tested, in the presence of the Engineer.  The test shall be performed in accordance with this item and prior to any activity affecting the respective circuit.  The Contractor shall record the results on forms acceptable to the engineer.  When the work affecting the circuit is complete, the circuit’s insulation resistance shall be checked again, in the presence of the Engineer.  The Contractor shall record the results on forms acceptable to the engineer.  The second reading shall be equal to or greater than the first reading or the Contractor shall make the necessary repairs to the circuit to bring the second reading above the first reading.  All repair costs including a complete replacement of the L-823 connectors, L-830 transformers and L-824 cable, if necessary, shall be borne by the Contractor.  All test results shall be submitted in the Operation and Maintenance (O&M) Manual.

# CONSTRUCTION

120-3.1  GENERAL.  The Contractor shall furnish, install, and connect all equipment, accessories, conduit, cables, wires, grounds, and supports necessary to ensure a complete and operable PAPI system as specified and as shown on the plans.

120-3.2  CONCRETE FOOTINGS.  Concrete footings and slabs shall be constructed as shown on the plans. Alternate footing designs may be used if approved. Anchor bolts shall be installed according to the manufacturer's recommendations.

120-3.3  INSTALLATION OF CABLE.  Underground cable for use between the PAPI units shall be installed as specified in Item MO-108 “Underground Power Cable for Airports” and shall be considered subsidiary to MO-120. No splices will be allowed in the cable runs. The minimum cover over the cable shall be 18 inches.

120-3.4  INSTALLATION OF PAPI UNITS.  The PAPI light units shall be installed on manufacturer supplied or recommended supports as shown on the plans. Manufacturer's instructions for installation shall be followed unless otherwise specified or directed by the Engineer.

A.  Azimuthal Aiming.  Each light unit shall be aimed outward into the approach zone on a line parallel to the runway centerline within a tolerance of ( 1/2 degree.

B.  Mounting Height Tolerances.  The beam centers of all light units in each system shall be within ( 1 inch of the elevation shown on the plans.

C.  Tolerance Along Line Perpendicular to Runway.  The front face of each light unit in a bar shall be located on a line perpendicular to the runway centerline within ( 6 inches.

120-3.5  ELECTRICAL CONNECTION.  The Contractor shall furnish all labor and materials and shall make complete electrical connections in accordance with the wiring diagram furnished with the plans.  The electrical installation shall conform to the requirements of the latest edition of National Fire Protection Association, NFPA-70, National Electric Code.

120-3.6  GROUND CONNECTION AND GROUND ROD.  The Contractor shall furnish and install a ground rod, grounding cable, and ground clamps for grounding each PAPI unit as shown on the plans.  The ground rod shall be of the type specified in Item MO-108 “Underground Power Cable for Airports and shall be of the length and diameter specified on the plans.  The ground rod shall be driven into the ground adjacent to the concrete foundation (minimum distance from foundation of 2 feet) so that the top is at least 6 inches below grade.  The grounding cable shall consist of No. 6 AWG minima bare stranded copper wire or larger and shall be firmly attached to the ground rod by exothermic welding per MO-108.  The other end of the grounding cable shall be securely attached to one mounting flange with non-corrosive metal and shall be of substantial construction.  The resistance to ground shall not exceed 25 ohms.

120-3.7  DELIVERY, STORAGE AND HANDLING.  Materials and equipment should be shipped disassembled to the extent necessary for reasons of: shipping limitations, handling facilities, and to avoid damage during shipment. Materials shall be maintained in new condition. This shall include suitable coverings, indoor storage, etc., to properly protect the equipment and materials.

Any equipment and materials, in the opinion of the Engineer, damaged during construction or storage shall be replaced by and at the cost of the Contractor. Painted and galvanized surfaces that are damaged shall be repaired according to manufacturer’s recommendations, to the satisfaction of the Engineer.

# METHOD OF MEASUREMENT

120-4.1  PAPI systems will be measured by the number of systems installed, ready for operation, and accepted by the Engineer. (One system consists of 4 light units for Type L-880). All footings, slabs, supports, conduits, trench, cable, ground rods, and connections necessary to install the system will not be measured separately, but shall be considered part of the system.

# BASIS OF PAYMENT

120-5.1  Payment will be made at the contract unit price per each 4-box PAPI system installed by the Contractor and accepted by the Engineer. This payment will be full compensation for furnishing all materials; for all preparation, assembly, and installation of these materials; and for all labor, equipment, tools and incidentals necessary to complete the item.

Payment will be made under:

MO-120-5.1	Airport PAPI-4 Box System -- per each

# MATERIAL REQUIREMENTS

Fed.Spec.W-C-1094	Conduit and Conduit Fittings; Plastic, Rigid (cancelled; replaced by UL 514 Boxes, Nonmetallic Outlet, Flush Device Boxes, & Covers, and UL 651 Standard for Conduit & Hope Conduit, Type EB & A Rigid PVC)

Underwriters Laboratories	Rigid Metal Conduit

Standard 6

Underwriters Laboratories	Fittings for Cable and Conduit

Standard 514B

Underwriters Laboratories	Intermediate Metal Conduit

Standard 1242

Underwriters Laboratories	Schedule 40 and 80 Rigid PVC Conduit (for Direct Burial)

Standard 651

Underwriters Laboratories	Type EB and A Rigid PVC Conduit and HDPE Conduit (for  Standard 651A	concrete encasement)

AC 150/5345-28	Precision Approach Path Indicator (PAPI) Systems.

AC 150/5345-42	Specification for Airport Light Bases, Transformer Housing, Junction Boxes, and Accessories

AC 150/5345-47	Isolation Transformers for Airport Light Systems

AC 150/5345-53	Airport Lighting Equipment Certification Program

REFERENCE DOCUMENTS

NFPA No. 70	National Electrical Code (NEC)